## Sheet1
TABLE VI
OPTIMIZATION AND DEPLOYMENT RESULTS OF THE THREE PLANNING METHODS
Algorithm | (\hat{F}_1) | (\hat{F}_2) | (\hat{F}_3) | (Z) | Active stations | Total chargers | Gap (%)
B&C | 0.15514 | 0.01749 | 0.08608 | -0.01765 | 8 | 188 | 0.001
BIPSO-GR | 0.20887 | 0.03312 | 0.20444 | 0.00883 | 6 | 333 | 0.009
Hybrid | 0.15514 | 0.01749 | 0.07959 | -0.01981 | 8 | 181 | 0.001
Algorithm | Active stations | 11 kW | 60 kW | 150 kW | Total chargers | Installed capacity (MW) | (P^{EVCS}) (MW) | (Q^{EVCS}) (MVAr) | HHI
B&C | 8 | 105 | 77 | 6 | 188 | 6.675 | 2.4173 | 0.4908 | 0.1736
BIPSO-GR | 6 | 91 | 240 | 2 | 333 | 15.701 | 5.5224 | 1.1214 | 0.2419
Hybrid | 8 | 99 | 79 | 3 | 181 | 6.279 | 2.2382 | 0.4545 | 0.1764
Algorithm | Raw (F_1) | Raw (F_2) | Raw (F_3) | (\hat{F}_1) | (\hat{F}_2) | (\hat{F}_3) | (Z) | Gap (%)
B&C | 80.85 | 255.15 | 1371.8 | 0.15514 | 0.01749 | 0.08608 | -0.017654 | 0.001409
BIPSO-GR | 108.85 | 483.35 | 3258.1 | 0.20887 | 0.03312 | 0.20444 | 0.008834 | 0.009142
Hybrid | 80.85 | 255.15 | 1268.3 | 0.15514 | 0.01749 | 0.07959 | -0.019812 | 0.001015

## README
EVCS GRID-IMPACT ANALYSIS — INPUT/OUTPUT WORKBOOK (v2)
Khai Nguyen — MPCE Q1 paper ¦ PowerWorld-ready MW + Mvar values
THAY ĐỔI SO VỚI v1
1. Bỏ hệ số dự phòng 1.2 (1.2 chỉ dùng để chọn dung lượng MBA, không phải tải vận hành)
2. Thêm cột MW và Mvar — copy thẳng vào dialog Load Options của PowerWorld
3. Đã verify với screenshot Bus 2 = 0.499 MW / 0.101 Mvar (cấu hình Hybrid hiện tại)
CÔNG THỨC TÍNH
MW = (N_11×11×SCF₁₁ + N_60×60×SCF₆₀ + N_150×150×SCF₁₅₀) / 0.98 / 1000
Mvar = MW × tan(arccos 0.98) = MW × 0.2031
HỆ SỐ SCF (từ Chương 4 luận văn)
11 kW (xe máy): SCF = 0.35
60 kW (avg EC/ET): SCF = 0.345
150 kW (xe buýt): SCF = 0.44
cosφ sau bù: 0.98
CẤU TRÚC FILE
Sheet 1_Charger_Configs | Số trụ tại 8 trạm × 3 thuật toán (Bảng 5.6, 5.7, 5.8 luận văn)
Sheet 2_EVCS_Loads | MW + Mvar tự tính cho 3 thuật toán (kết quả chính)
Sheet 3_Scenarios | Danh sách 15 trường hợp cần chạy
Sheet 4_PowerWorld_Inputs | BẢNG QUAN TRỌNG NHẤT — copy từ đây vào PowerWorld
Sheet 5_Results_Template | Bảng trống ghi V_min, %loading, P_loss sau mỗi lần chạy
QUY ƯỚC MÀU
Xanh dương nhạt | Cột MW (Constant Power)
Vàng | Cột Mvar (Constant Power)
Xanh lá | Cấu hình Hybrid base case — đã chạy xong trong luận văn
Cam | Ô trống cần điền sau khi chạy PowerWorld
CÁCH ĐIỀN VÀO POWERWORLD
Bus 2: Right-click → Load Options → Load Information tab
→ MW Value (Constant Power column) = giá trị MW từ Sheet 4
→ Mvar Value (Constant Power column) = giá trị Mvar từ Sheet 4
→ Constant Current = 0.000 (giữ nguyên)
→ Constant Impedance = 0.000 (giữ nguyên)
Lặp lại cho Bus 4, 6, 8, 10, 13, 14, 15
THỨ TỰ CHẠY 14 LẦN CÒN LẠI
Bước 1 (1 giờ) | Base case 2 thuật toán còn lại: S1-BC, S1-HB
Bước 2 (3 giờ) | N-1 mất S1: S2-BC, S2-HB, S2-HY
Bước 3 (3 giờ) | N-1 mất S2: S3-BC, S3-HB, S3-HY
Bước 4 (2 giờ) | Sensitivity ×1.2: S4-BC, S4-HB, S4-HY
Bước 5 (2 giờ) | Sensitivity ×1.5: S5-BC, S5-HB, S5-HY

## 1_Charger_Configs
CHARGER ALLOCATION BY STATION (units) — from Thesis Tables 5.6, 5.7, 5.8
Station | Bus | TBA | B&C |  |  | BIPSO-GR |  |  | Hybrid |  |  | Status
|  |  | 11kW | 60kW | 150kW | 11kW | 60kW | 150kW | 11kW | 60kW | 150kW
CC-TM2 | 2 | T10 | 20 | 6 | 0 | 25 | 37 | 0 | 17 | 5.5 | 0
CC-TLC | 4 | T14 | 15 | 8 | 0 | 0 | 25 | 0 | 14.5 | 8 | 0
CC-HH2 | 6 | T13 | 12 | 21 | 0 | 25 | 75 | 0 | 12 | 32.5 | 0
CC-TT1 | 8 | T9 | 12 | 6 | 0 | 0 | 0 | 0 | 11.75 | 6 | 0 | BIPSO-GR closed
CC-TM1 | 10 | T8 | 16 | 9 | 0 | 25 | 80 | 0 | 16 | 9 | 0
CC-HH1 | 13 | T7 | 10 | 6 | 0 | 3 | 2 | 0 | 10.25 | 5.5 | 0
CC-BDX | 14 | T12 | 10 | 14 | 6 | 13 | 21 | 2 | 6.75 | 4 | 3
CC-TM3 | 15 | T11 | 10 | 7 | 0 | 0 | 0 | 0 | 10 | 6.5 | 0 | BIPSO-GR closed
TOTAL |  |  | 105 | 77 | 6 | 91 | 240 | 2 | 98.25 | 77 | 3

## 2_EVCS_Loads
EVCS LOAD AT EACH BUS — MW (Constant Power) + Mvar — ready for PowerWorld
Formula: MW = (N₁₁×11×0.35 + N₆₀×60×0.345 + N₁₅₀×150×0.44) / 0.98 / 1000 ¦ Mvar = MW × 0.2031
NO 1.2 reserve factor (operational load, not transformer sizing) ¦ cosφ = 0.98 after compensation
Constants
SCF 11kW (EM) | 0.35
SCF 60kW (avg EC/ET) | 0.345
SCF 150kW (EB) | 0.44
cosφ (after comp.) | 0.98
tanφ = sin/cos | 0.2031
Station | Bus | TBA | B&C |  | BIPSO-GR |  | Hybrid |  | Verification (Hybrid)
|  |  | MW | Mvar | MW | Mvar | MW | Mvar | Appendix kW | Calc kW | Diff %
CC-TM2 | 2 | T10 | 0.20531 | 0.041698 | 0.87974 | 0.17868 | 0.18296 | 0.037159 | 587 | 215.16 | 63.3458
CC-TLC | 4 | T14 | 0.22791 | 0.046288 | 0.52806 | 0.10725 | 0.22594 | 0.045889 | 665.4 | 265.71 | 60.0676
CC-HH2 | 6 | T13 | 0.49071 | 0.099664 | 1.6824 | 0.3417 | 0.73362 | 0.149 | 1838.2 | 862.74 | 53.066
CC-TT1 | 8 | T9 | 0.17388 | 0.035315 | 0 | 0 | 0.1729 | 0.035115 | 519.5 | 203.325 | 60.8614
CC-TM1 | 10 | T8 | 0.25296 | 0.051376 | 1.788 | 0.36314 | 0.25296 | 0.051376 | 742.8 | 297.48 | 59.9515
CC-HH1 | 13 | T7 | 0.16602 | 0.033719 | 0.054031 | 0.010974 | 0.15644 | 0.031773 | 462.3 | 183.975 | 60.2044
CC-BDX | 14 | T12 | 0.73908 | 0.15011 | 0.62934 | 0.12782 | 0.31305 | 0.06358 | 801.5 | 368.145 | 54.068
CC-TM3 | 15 | T11 | 0.18714 | 0.038009 | 0 | 0 | 0.17658 | 0.035864 | 508.1 | 207.66 | 59.1301
TOTAL |  |  | 2.443 | 0.49618 | 5.5616 | 1.1296 | 2.2145 | 0.44976
Verification: 'Calc kW' = MW × 1000 × cosφ × 1.2 should match Appendix 6. Diff < 1% confirms correct calculation.

## 3_Scenarios
SCENARIO LIST — 15 PowerWorld runs
# | Scenario ID | Algorithm | Source state | Multiplier | Description | Priority | Status
1 | S1-BC | B&C | Both S1+S2 | 1 | Base case — both sources OK | Done | ✓ Completed
2 | S1-HB | BIPSO-GR | Both S1+S2 | 1 | Base case — both sources OK | Done | ✓ Completed
3 | S1-HY | Hybrid | Both S1+S2 | 1 | Base case — both sources OK (DONE in thesis) | Done | ✓ Completed
4 | S2-BC | B&C | S1 lost | 1 | N-1: lose S1, S2 carries all (close N.O. 3-4) | 1 — High | ✓ Completed
5 | S2-HB | BIPSO-GR | S1 lost | 1 | N-1: lose S1, S2 carries all (close N.O. 3-4) | 1 — High | ✓ Completed
6 | S2-HY | Hybrid | S1 lost | 1 | N-1: lose S1, S2 carries all (close N.O. 3-4) | 1 — High | ✓ Completed
7 | S3-BC | B&C | S2 lost | 1 | N-1: lose S2, S1 carries all (close N.O. 3-4) | 1 — High | ✓ Completed
8 | S3-HB | BIPSO-GR | S2 lost | 1 | N-1: lose S2, S1 carries all (close N.O. 3-4) | 1 — High | ✓ Completed
9 | S3-HY | Hybrid | S2 lost | 1 | N-1: lose S2, S1 carries all (close N.O. 3-4) | 1 — High | ✓ Completed
10 | S4-BC | B&C | Both S1+S2 | 1.2 | Sensitivity ×1.2 — seasonal tourism peak | 2 — Med | ✓ Completed
11 | S4-HB | BIPSO-GR | Both S1+S2 | 1.2 | Sensitivity ×1.2 — seasonal tourism peak | 2 — Med | ✓ Completed
12 | S4-HY | Hybrid | Both S1+S2 | 1.2 | Sensitivity ×1.2 — seasonal tourism peak | 2 — Med | ✓ Completed
13 | S5-BC | B&C | Both S1+S2 | 1.5 | Sensitivity ×1.5 — APEC-like event stress | 2 — Med | ✓ Completed
14 | S5-HB | BIPSO-GR | Both S1+S2 | 1.5 | Sensitivity ×1.5 — APEC-like event stress | 2 — Med | ✓ Completed
15 | S5-HY | Hybrid | Both S1+S2 | 1.5 | Sensitivity ×1.5 — APEC-like event stress | 2 — Med | ✓ Completed

## 4_PowerWorld_Inputs
POWERWORLD INPUT TABLE — MW & Mvar pairs ready to copy into Load Options dialog
Each row = 1 PowerWorld run. For each bus, copy MW into 'MW Value' and Mvar into 'Mvar Value' (Constant Power column).
Scenario | Algo | Source | Mult | Bus 2 — CC-TM2 |  | Bus 4 — CC-TLC |  | Bus 6 — CC-HH2 |  | Bus 8 — CC-TT1 |  | Bus 10 — CC-TM1 |  | Bus 13 — CC-HH1 |  | Bus 14 — CC-BDX |  | Bus 15 — CC-TM3
|  |  |  | MW | Mvar | MW | Mvar | MW | Mvar | MW | Mvar | MW | Mvar | MW | Mvar | MW | Mvar | MW | Mvar
S1-BC | B&C | Both S1+S2 | 1 | 0.20531 | 0.041698 | 0.22791 | 0.046288 | 0.49071 | 0.099664 | 0.17388 | 0.035315 | 0.25296 | 0.051376 | 0.16602 | 0.033719 | 0.73908 | 0.15011 | 0.18714 | 0.038009 | Done
S1-HB | BIPSO-GR | Both S1+S2 | 1 | 0.87974 | 0.17868 | 0.52806 | 0.10725 | 1.6824 | 0.3417 | 0 | 0 | 1.788 | 0.36314 | 0.054031 | 0.010974 | 0.62934 | 0.12782 | 0 | 0 | Done
S1-HY | Hybrid | Both S1+S2 | 1 | 0.18296 | 0.037159 | 0.22594 | 0.045889 | 0.73362 | 0.149 | 0.1729 | 0.035115 | 0.25296 | 0.051376 | 0.15644 | 0.031773 | 0.31305 | 0.06358 | 0.17658 | 0.035864 | Done
S2-BC | B&C | S1 lost | 1 | 0.20531 | 0.041698 | 0.22791 | 0.046288 | 0.49071 | 0.099664 | 0.17388 | 0.035315 | 0.25296 | 0.051376 | 0.16602 | 0.033719 | 0.73908 | 0.15011 | 0.18714 | 0.038009 | Done
S2-HB | BIPSO-GR | S1 lost | 1 | 0.87974 | 0.17868 | 0.52806 | 0.10725 | 1.6824 | 0.3417 | 0 | 0 | 1.788 | 0.36314 | 0.054031 | 0.010974 | 0.62934 | 0.12782 | 0 | 0 | Done
S2-HY | Hybrid | S1 lost | 1 | 0.18296 | 0.037159 | 0.22594 | 0.045889 | 0.73362 | 0.149 | 0.1729 | 0.035115 | 0.25296 | 0.051376 | 0.15644 | 0.031773 | 0.31305 | 0.06358 | 0.17658 | 0.035864 | Done
S3-BC | B&C | S2 lost | 1 | 0.20531 | 0.041698 | 0.22791 | 0.046288 | 0.49071 | 0.099664 | 0.17388 | 0.035315 | 0.25296 | 0.051376 | 0.16602 | 0.033719 | 0.73908 | 0.15011 | 0.18714 | 0.038009 | Done
S3-HB | BIPSO-GR | S2 lost | 1 | 0.87974 | 0.17868 | 0.52806 | 0.10725 | 1.6824 | 0.3417 | 0 | 0 | 1.788 | 0.36314 | 0.054031 | 0.010974 | 0.62934 | 0.12782 | 0 | 0 | Done
S3-HY | Hybrid | S2 lost | 1 | 0.18296 | 0.037159 | 0.22594 | 0.045889 | 0.73362 | 0.149 | 0.1729 | 0.035115 | 0.25296 | 0.051376 | 0.15644 | 0.031773 | 0.31305 | 0.06358 | 0.17658 | 0.035864 | Done
S4-BC | B&C | Both S1+S2 | 1.2 | 0.24637 | 0.050037 | 0.27349 | 0.055546 | 0.58886 | 0.1196 | 0.20865 | 0.042377 | 0.30355 | 0.061651 | 0.19922 | 0.040462 | 0.8869 | 0.18013 | 0.22457 | 0.04561 | Done
S4-HB | BIPSO-GR | Both S1+S2 | 1.2 | 1.0557 | 0.21441 | 0.63367 | 0.1287 | 2.0189 | 0.41003 | 0 | 0 | 2.1456 | 0.43577 | 0.064837 | 0.013168 | 0.7552 | 0.15338 | 0 | 0 | Done
S4-HY | Hybrid | Both S1+S2 | 1.2 | 0.21955 | 0.044591 | 0.27113 | 0.055067 | 0.88035 | 0.1788 | 0.20747 | 0.042138 | 0.30355 | 0.061651 | 0.18773 | 0.038128 | 0.37566 | 0.076296 | 0.2119 | 0.043036 | Done
S5-BC | B&C | Both S1+S2 | 1.5 | 0.30796 | 0.062547 | 0.34186 | 0.069432 | 0.73607 | 0.1495 | 0.26082 | 0.052972 | 0.37944 | 0.077064 | 0.24903 | 0.050578 | 1.1086 | 0.22516 | 0.28071 | 0.057013
S5-HB | BIPSO-GR | Both S1+S2 | 1.5 | 1.3196 | 0.26801 | 0.79209 | 0.16087 | 2.5236 | 0.51254 | 0 | 0 | 2.682 | 0.54472 | 0.081046 | 0.01646 | 0.94401 | 0.19173 | 0 | 0
S5-HY | Hybrid | Both S1+S2 | 1.5 | 0.27444 | 0.055739 | 0.33892 | 0.068834 | 1.1004 | 0.2235 | 0.25934 | 0.052673 | 0.37944 | 0.077064 | 0.23466 | 0.04766 | 0.46957 | 0.09537 | 0.26487 | 0.053796
Notes:
• N-1 (S2, S3): Open generator at lost source bus, AND close N.O. switch between Bus 3-4 (so S2 or S1 alone can serve all loads).
• HBIPSO-GR: Bus 8 (CC-TT1) and Bus 15 (CC-TM3) have zero load — these stations are closed in optimization.
• Hybrid base case (S1-HY) already completed — green row shows reference values.
• In PowerWorld Load Options dialog: MW Value = 'MW' column, Mvar Value = 'Mvar' column (both under 'Constant Power' header).
• Constant Current and Constant Impedance fields stay at 0.000.

## 5_Results_Template
RESULTS TEMPLATE — fill after each PowerWorld run
After each NR power flow, record V_min, max feeder loading, total losses, and check violations.
Scenario | Algo | Source | Mult | V_min (p.u.) | Bus of V_min | Max %S loading | Branch of max loading | P_loss (kW) | Violation? (Y/N) | Notes
S1-BC | B&C | Both S1+S2 | 1 | 0.9994 | Bus 16 (T5) | 61.1 | S1 to T10 |  | N
S1-HB | BIPSO-GR | Both S1+S2 | 1 | 0.9993 | Bus 16 (T5) | 80.8 | S1 to T10 |  | N
S1-HY | Hybrid | Both S1+S2 | 1 | 0.9994 | Bus 16 (T5) | 60.8 | S1 to T10 |  | N
S2-BC | B&C | S1 lost | 1 | 0.9978 | Bus 13 (T7) | 118.6 | T13 to S2 |  | Y | T6 to T13 (103.2)
S2-HB | BIPSO-GR | S1 lost | 1 | 0.9973 | Bus 13 (T7) | 157.3 | T13 to S2 |  | Y | T6 to T13 (122.9)
S2-HY | Hybrid | S1 lost | 1 | 0.9979 | Bus 13 (T7) | 116.2 | T13 to S2 |  | Y
S3-BC | B&C | S2 lost | 1 | 0.9986 | Bus 16 (T5) | 118.5 | S1 to T10 |  | Y
S3-HB | BIPSO-GR | S2 lost | 1 | 0.9983 | Bus 6 (T13) | 157.2 | S1 to T10 |  | Y
S3-HY | Hybrid | S2 lost | 1 | 0.9987 | Bus 16 (T5) | 116.2 | S1 to T10 |  | Y
S4-BC | B&C | Both S1+S2 | 1.2 | 0.9994 | Bus 16 (T5) | 62.8 | S1 to T10 |  | N
S4-HB | BIPSO-GR | Both S1+S2 | 1.2 | 0.9993 | Bus 16 (T5) | 86.3 | S1 to T10 |  | N
S4-HY | Hybrid | Both S1+S2 | 1.2 | 0.9994 | Bus 16 (T5) | 62.4 | S1 to T10 |  | N
S5-BC | B&C | Both S1+S2 | 1.5 | 0.9994 | Bus 16 (T5) | 65.2 | S1 to T10 |  | N
S5-HB | BIPSO-GR | Both S1+S2 | 1.5 | 0.9993 | Bus 16 (T5) | 94.7 | S1 to T10 |  | N
S5-HY | Hybrid | Both S1+S2 | 1.5 | 0.9994 | Bus 16 (T5) | 64.7 | S1 to T10 |  | N
QUICK ANALYSIS QUESTIONS — answer after data is filled:
Q1 — Base case (S1): Which algorithm has the highest max feeder loading? Compare with HBIPSO-GR's concentrated CC-TM1 load (1.75 MW at Bus 10).
Q2 — N-1 (S2, S3): Are there violations? When S2 is lost, S1 must feed everything alone — does any algorithm fail?
Q3 — Sensitivity (S4, S5): At ×1.5 multiplier, does any algorithm exceed 100% loading?
Q4 — Pattern: Do distributed layouts (B&C, Hybrid) consistently outperform concentrated (HBIPSO-GR) under stress?